## หน้าปก
Report PM Fire Protection 3/3
ประจำปี 2566
บริษัท ดิ เอราวัณ กรุ๊ป จำกัด (มหาชน)
โครงการ Holiday Inn Pattaya Bay Tower
วันที่ 13 ธันวาคม 2566
โดย
SYSTEMS SERVICE DEPARTMENT
THE SOLUTION TO SERVE YOUR PROBLEMS
บริษัท ดู ออล อาคิเทค แอนด์ เอ็นจิเนียริ่ง จำกัด
68/155 หมู่ 3 ถนนชัยพฤกษ์ ตำบลคลองพระอุดม อำเภอปากเกร็ด จังหวัด นนทบุรี 11120
Email: info.doall.ae@gmail.com โทร.082-069-0919
68/155 Moo 3 Chaiyaphruek Road, Khlong Phra Udom, Pak Kret t, Nonthaburi 11120
Email: info.doall.ae@gmail.com Tel. 082-069-0919

## ใบปะหน้า
บริษัท ดู ออล อาคิเทค แอนด์ เอ็นจิเนียริ่ง จำกัด
DO ALL ARCHITECH AND ENGINEERING CO.,LTD.
สำนักงานใหญ่ : 68/155 หมู่ 3 ถนนชัยพฤกษ์ ตำบลคลองพระอุดม อำเภอปากเกร็ด จังหวัด นนทบุรี 11120
เลขประจำตัวผู้เสียภาษี 0125563014222
เลขที่ | 0014/2566
วันที่ | 2023-12-13
เรื่อง | ส่งมอบเอกสารการบำรุงรักษาระบบ Fire Protection
โครงการ | Holiday Inn Pattaya Bay Tower
บริษัท ดิ เอราวัณ กรุ๊ป จำกัด (มหาชน)
สำนักงานสาขาตั้งอยู่เลขที่ 463/68,463/99 อาคารโรงแรมฮอลิเดย์ อินน์ พัทยา ถนนพัทยาสาย 1 ตำบลหนองปรือ
อำเภอบางละมุง จังหวัดชลบุรี
เรียน | โรงแรม Holiday Inn Pattaya
สิ่งที่ส่งมาด้วย
1. เอกสารการบำรุงรักษาระบบ Fire Protection จำนวน 1 ชุด
เนื่องจากการดำเนินการบำรุงรักษาระบบ Fire Protection
โครงการ Holiday Inn Pattaya Bay Tower ได้ดำเนินการเสร็จสิ้นแล้วในวันที่ 13 ธันวาคม 2566
ตามเอกสารรายงานการบริการที่ส่งมาด้วยนี้ บริษัท ดู ออล อาคิเทค แอนด์ เอ็นจิเนียริ่ง จำกัด จึงใคร่ขอส่งมอบเอกสารงานบริการ
ตรวจสอบและบำรุงรักษาระบบ Fire Protection โครงการ Holiday Inn Pattaya Bay Tower ทั้งหมด
ให้กับท่านเพื่อพิจารณาและลงนามรับมอบด้วย จักขอบพระคุณยิ่ง
จึงเรียนมาเพื่อทราบและโปรดพิจารณา
| ลงนามตรวจสอบและรับเอกสาร |  |  | ขอแสดงความนับถือ
| …………………………………………… |  |  | ( นายธนภัทร ยั่งยืน )
| (______________________________) |  |  | วิศวกรฝ่ายขาย
| วันที่________/_________/_________ |  | บริษัท ดู ออล อาคิเทค แอนด์ เอ็นจิเนียริ่ง จำกัด
บริษัท ดิ เอราวัณ กรุ๊ป จำกัด (มหาชน)

## Control (hidden)
บริษัท ดู ออล อาคิเทค แอนด์ เอ็นจิเนียริ่ง จำกัด
68/155 หมู่ 3 ถนนชัยพฤกษ์ ตำบลคลองพระอุดม อำเภอปากเกร็ด จังหวัด นนทบุรี 11120
Email: info.doall.ae@gmail.com โทร.082-069-0919
Preventive Maintenance Report
General Information
Project |  | : | Holiday Inn Pattaya Bay Tower | System : |  |  | Fire Alarm | [5 empty] | Model : EST3
Revision |  | : | - | Manufacturer : |  |  | Notify
PM No. |  | : | ครั้งที่ 1 ประจำปี 2566 | Start : |  |  | 243283 |  |  |  |  | End : 3 ก.พ. 66
Parts / Devices Types
Part/Dev. |  | : | FCP. | Installed by : |  |  | -
Location |  | : | CCTV Room | Inspected by : |  |  |  | Do All CO.,LTD.
Inspections and Tests List
Item | Descriptions |  |  |  | Check |  |  | Functional | [5 empty] | Remarks
[5 empty] | Installation | Wiring | Cleaning | Alarm | Suppervisory | Trouble | Monitor | Operation.
FAP
01 | Power Supplies
| 1.01 | 3-PPS Primary Power Supply |  |  | / | / | / | - | - | - | - | / |  | -
|  | > AC Power Input (220 Vac) |  |  | / | / | / | - | - | - | - | / |  | -
|  | > DC Power Connector to 3-PSMON |  |  | / | / | / | - | - | / | - | - |  | -
|  | > 16 Pin data line connector to 3-PSMON |  |  | / | / | / | - | - | - | - | / |  | -
|  | > Battery connector |  |  | / | / | / | - | - | - | - | / |  | -
| 1.02 | 3-PSMON Primary Power Supply Monitor module |  |  | / | / | / | - | - | - | - | / |  | -
|  | > DC Power Connector from 3-PPS |  |  | / | / | / | - | - | - | - | / |  | -
|  | > 16- pin data conector from 3-PPS |  |  | / | / | / | - | - | - | - | / |  | -
|  | > 24 VDC Auxiliary power & connector. (2 Output) |  |  | / | / | / | - | - | - | - | / |  | -
02 | 3-CPU1
| 2.01 | > Data Network Riser Next CPU |  |  | / | / | / | - | - | - | - | / |  | -
| 2.02 | > Data Network Riser Conections (RS-485). |  |  | / | / | / | - | - | / | - | - |  | -
| 2.03 | > RS-232 Conection. |  |  | / | / | / | - | - | - | - | / |  | -
03 | 3-SSDC,3-SDDC Signature Device Controller
| 3.01 | > Signature Circuit Connections. |  |  | / | / | / | - | - | - | - | / |  | Loop1,2
| 3.02 | > Filter Board |  |  | / | / | / | - | - | - | - | / |  | -
04 | Battery Charger
| 4.01 | > Battery Backup For FCP (12 Vdc.@ 12 Amp. 1 Set.) |  |  | / | / | / | - | - | / | - | - |  | -
05 | Indicator Lamps (At 3-LCD)
| 5.01 | > Alarm |  |  | / | / | / | - | - | - | - | / |  | -
| 5.02 | > Suppervisory |  |  | / | / | / | - | - | - | - | / |  | -
| 5.03 | > Trouble |  |  | / | / | / | - | - | - | - | / |  | -
| 5.04 | > Monitor |  |  | / | / | / | - | - | - | - | / |  | -
| 5.05 | > Power |  |  | / | / | / | - | - | - | - | / |  | -
| 5.06 | > Test |  |  | / | / | / | - | - | - | - | / |  | -
| 5.07 | > CPU Fail |  |  | / | / | / | - | - | - | - | / |  | -
| 5.08 | > Gnd Fault |  |  | / | / | / | - | - | - | - | / |  | -
| 5.09 | > Disable |  |  | / | / | / | - | - | - | - | / |  | -
06 | Control Switches (At 3-LCD)
| 6.01 | > Reset |  |  | / | / | / | - | - | - | - | / |  | -
| 6.02 | > Alarm Silence |  |  | / | / | / | - | - | - | - | / |  | -
| 6.03 | > Drill |  |  | / | / | / | - | - | - | - | / |  | -
| 6.04 | > Panal Silence |  |  | / | / | / | - | - | - | - | / |  | -
| 6.05 | > Alarm |  |  | / | / | / | - | - | - | - | / |  | -
| 6.06 | > Suppervisory |  |  | / | / | / | - | - | - | - | / |  | -
| 6.07 | > Trouble |  |  | / | / | / | - | - | - | - | / |  | -
| 6.08 | > Monitor |  |  | / | / | / | - | - | - | - | / |  | -
| 6.09 | > 0-9 |  |  | / | / | / | - | - | - | - | / |  | -
| 6.10 | > ENTER |  |  | / | / | / | - | - | - | - | / |  | -
| 6.11 | > DEL. |  |  | / | / | / | - | - | - | - | / |  | -
| 6.12 | > Detail |  |  | / | / | / | - | - | - | - | / |  | -
| 6.13 | > Message Next |  |  | / | / | / | - | - | - | - | / |  | -
| 6.14 | > Command Manu |  |  | / | / | / | - | - | - | - | / |  | -
07 | 3-FTCU Controller ( Control Switches) |  |  |  | / | / | / | - | - | - | - | / |  | -
| 7.01 | > Connect sw. |  |  | / | / | / | - | - | - | - | / |  | -
| 7.02 | > Review Pending sw. |  |  | / | / | / | - | - | - | - | / |  | -
| 7.03 | > ACK SW |  |  | / | / | / | - | - | - | - | / |  | -
| 7.04 | > Disconnect |  |  | / | / | / | - | - | - | - | / |  | -
| 7.05 | > Review Connected. |  |  | / | / | / | - | - | - | - | / |  | -
08 | LCD Display |  |  |  | / | / | / | - | - | - | - | / |  | -
09 | Trouble,Alarm Buzzer |  |  |  | / | / | / | - | - | - | - | / |  | -
10 | Computer Graphic at Operator Engineering Room |  |  |  | / | / | / | - | - | - | - | / |  | -

## H1
บริษัท ดู ออล อาคิเทค แอนด์ เอ็นจิเนียริ่ง จำกัด
68/155 หมู่ 3 ถนนชัยพฤกษ์ ตำบลคลองพระอุดม อำเภอปากเกร็ด จังหวัด นนทบุรี 11120
Email: info.doall.ae@gmail.com โทร.082-069-0919
Report PM Fire Protection 3/3
Holiday Inn Pattaya
Photo # 01 Testing date 13/12/2022
Topic : Flow switch testing
Area : LP Service Lift, Stairs
Details : - Flow switch functional testing at Fire protection shaft by connect of limit switch. - Flow switch response between 30-60 seconds. - Labeled the flow switch that passed the performance testing.
Photo # 01 Testing date 13/12/2022
Topic : Supervisory switch testing
Area : LP Service Lift, Stairs
Details : - Supervisory switch functional testing at Fire protection shaft by close valve. - Supervisory switch response between ¼ turn – 1 turn. - Labeled the supervisory switch that passed the performance testing.
Location | Type Code | Label | Alarm Tested | Graphic Com. | Remark
Fl.26 | Flow | N02L05M088
| Flow | N02L05M094
| Supervisory | N02L05M095
| Supervisory | N02L05M085
| Flow | N02L05M086
| Flow | N02L05M087
| Flow | N02L05M084
| Supervisory | N02L05M083
Fl.25 | Flow | N02L04M102
| Supervisory | N02L04M106
| Flow | N02L04M104
| Flow | N02L04M105
| Flow | N02L04M103
| Supervisory | N02L04M107
Fl.24 | Flow | N02L04M096
| Flow | N02L04M094
| Supervisory | N02L04M098
| Flow | N02L04M095
| Flow | N02L04M093
| Supervisory | N02L04M097
Fl.23 | Flow | N02L04M084
| Supervisory | N02L04M088
| Flow | N02L04M086
| Flow | N02L04M087
| Flow | N02L04M085
| Supervisory | N02L04M089
Fl.22 | Flow | N02L03M105
| Flow | N02L03M103
| Supervisory | N02L03M107
| Flow | N02L03M104
| Flow | N02L03M102
| Supervisory | N02L03M106
Fl.21 | Flow | N02L03M093
| Supervisory | N02L03M097
| Flow | N02L03M095
| Flow | N02L03M096
| Flow | N02L03M094
| Supervisory | N02L03M098
Fl.20 | Flow | N02L03M087
| Flow | N02L03M085
| Supervisory | N02L03M089
| Flow | N02L03M086
| Flow | N02L03M084
| Supervisory | N02L03M88
Fl.19 | Flow | N02L02M102
| Supervisory | N02L02M106
| Flow | N02L02M104
| Flow | N02L02M105
| Flow | N02L02M103
| Supervisory | N02L02M107
Fl.18 | Flow | N02L02M096
| Flow | N02L02M094
| Supervisory | N02L02M098
| Flow | N02L02M095
| Flow | N02L02M093
| Supervisory | N02L02M097
Fl.17 | Flow | N02L02M084
| Supervisory | N02L02M088
| Flow | N02L02M086
| Flow | N02L02M087
| Flow | N02L02M085
| Supervisory | N02L02M089
Fl.16 | Flow | N02L01M105
| Flow | N02L01M103
| Supervisory | N02L01M107
| Flow | N02L01M104
| Flow | N02L01M102
| Supervisory | N02L01M106
Fl.15 | Flow | N02L01M093
| Supervisory | N02L01M097
| Flow | N02L01M095
| Flow | N02L01M096
| Flow | N02L01M094
| Supervisory | N02L01M098
Fl.14 | Flow | N02L01M087
| Flow | N02L01M085
| Supervisory | N02L01M089
| Flow | N02L01M086
| Flow | N02L01M084
| Supervisory | Fl.12+A311:A319
Fl.12 | Flow | N01L06M105
| Flow | N01L06M103
| Supervisory | N01L06M107
| Flow | N01L06M104
| Flow | N01L06M102
| Supervisory | N01L06M106
Fl.11 | Flow | N01L06M093
| Supervisory | N01L06M097
| Flow | N01L06M095
| Flow | N01L06M096
| Flow | N01L06M094
| Supervisory | N01L06M098
Fl.10 | Flow | N01L06M087
| Flow | N01L06M085
| Supervisory | N01L06M089
| Flow | N01L06M086
| Flow | N01L06M084
| Supervisory | N01L06M088
Fl.9 | Flow | N01L05M102
| Supervisory | N01L05M106
| Flow | N01L05M104
| Flow | N01L05M105
| Flow | N01L05M103
| Supervisory | N01L05M107
FL.8 | Flow | N01L05M096
| Flow | N01L05M094
| Supervisory | N01L05M098
| Flow | N01L05M095
| Flow | N01L05M093
| Supervisory | N01L05M097
FL.7 | Flow | N01L05M088
| Supervisory | N01L05M088
| Flow | N01L05M086
| Flow | N01L05M087
| Flow | N01L05M085
| Supervisory | N01L05M089
FL.6 | Flow | N0L04M121
| Flow | N01L04M119
| Flow | N01L04M124
| Supervisory | N01L04M123
| Supervisory | N01L04M130
| Flow | N01L04M120
| Flow | N01L04M118
| Flow | N01L04M122
FL.5 | Flow | N01L04M103
| Flow | N01L04M101
| Flow | N01L04M125
| Flow | N01L05M117
| Supervisory | N01L04M106
| Supervisory | N01L04M126
| Flow | N01L04M104
| Flow | N01L04M100
| Supervisory | N01L04M100
FL.TR | Supervisory | N01L04M113
| Supervisory | N01L04M113
| Flow | N01L04M109
FL.5 | Flow | N01L04M090
| Supervisory | N01L04M094
FL.4 | Flow | N01L04M085
| Flow | N01L04M084
| Flow | N01L04M083
| Supervisory | N01L04M087
| Flow | N01L04M086
FL.M | Flow | N01L04M086
| Flow | N01L03M129
| Flow | N01L03M127
| Flow | N01L03M102
| Flow | N01L03M101
| Supervisory | N01L03M108
| Supervisory | N01L03M133
| Supervisory | N01L03M131
| Flow | N01L03M130
| Flow | N01L03M128
| Supervisory | N01L03M132

## Sheet1
บริษัท ดู ออล อาคิเทค แอนด์ เอ็นจิเนียริ่ง จำกัด
68/155 หมู่ 3 ถนนชัยพฤกษ์ ตำบลคลองพระอุดม อำเภอปากเกร็ด จังหวัด นนทบุรี 11120
Email: info.doall.ae@gmail.com โทร.082-069-0919
Report PM Fire Protection 3/3
รูปภาพการทดสอบ